A Self-Calibrating Approach to Whole-Home   
Contactless Power Consumption Sensing

| 1st Author Name  Affiliation  Address  e-mail address  Optional phone number | 2nd Author Name  Affiliation  Address  e-mail address  Optional phone number | 3rd Author Name  Affiliation  Address  e-mail address  Optional phone number |
| --- | --- | --- |

# ABSTRACT

Paste the appropriate copyright/license statement here. ACM now supports three different publication options:

* ACM copyright: ACM holds the copyright on the work. This is the historical approach.
* License: The author(s) retain copyright, but ACM receives an exclusive publication license.
* Open Access: The author(s) wish to pay for the work to be open access. The additional fee must be paid to ACM.

This text field is large enough to hold the appropriate release statement assuming it is single-spaced in TimesNewRoman 8 point font. Please do not change or modify the size of this text box.

In this paper, we present a significant improvement over past work on non-contact end-user deployable sensor for real time whole home power consumption. The technique allows users to place a single device consisting of magnetic pickups on the outside of a power or breaker panel to infer whole home power consumption without the need for professional installation of current transformers (CTs). The new approach does not require precise placement on the breaker panel, a key requirement in previous approaches. This is enabled through a self-calibration technique using a neural network that dynamically learns the transfer function despite the placement of the sensor and the construction of the breaker panel itself. We also demonstrate the ability to actually infer *true power* using this technique, unlike past solutions that have only been able to capture *apparent power*. We have evaluated our technique in six homes and one industrial building, including one seven-day deployment. Our results show we can estimate true power consumption with an average accuracy of 95.0% during naturalistic energy use in the home.

## Author Keywords

Energy monitoring; sustainability sensing; smart home; ubiquitous computing

## ACM Classification Keywords

H.5.m. Information interfaces and presentation (*e.g*., HCI): Miscellaneous.

# INTRODUCTION


Energy conservation and eco-feedback research continues to be an important focus in the Ubicomp and HCI communities. Given that 28% of U.S. energy consumption is directly contributed by household activities [3], the home is a natural place to study. However, just obtaining whole home power consumption information in real-time by 

Figure 1: *Left:* Contactless power consumption sensor on the breaker panel; *Right:* An interface showing whole-home total power consumption in real-time.

homeowners or even researchers is not a simple task. For instance, certain smart meters provide data at 15 minutes intervals, however gaining access to that information is challenging due to closed-source and often private protocols and application interfaces. The most common approach to date is to install commercially available CTs inside the breaker panel. However, safely installing this device requires hiring a trained electrician as it involves placing a sensor around the main electrical feed in the breaker panel. Most researchers and homeowners do not have the training or confidence to do such an installation. In fact, the National Electric Code (NEC) has strict rules on the requirement of professional installation of CTs. In addition, certain U.S. states disallow CTs to be installed inside the breaker panel at all, in which case an expensive pass through meter solution is required. The latter requires involvement of the utility company as an end-user cannot tamper with or alter the installation of an electricity meter.

To address this challenge, in previous work Patel *et al.* [11] introduced a contactless power consumption sensor that reduces such deployment burdens by offering a “stick on” sensor that goes on the outside of the breaker panel. This technique utilized magnetic sensors to sense the magnetic field induced by the 60Hz current flowing through the main lines inside the breaker panel. While this initial work was a step towards simple and easy to deploy non-intrusive power monitoring, there are some important limitations to consider. First, the existing approach requires the user to precisely position the sensor on the panel, which is a difficult task for an end-user to perform. Second, the approach assumed a linear transfer function between the magnetic sensors and the current, which limits it’s accuracy to a small current range. Third, the approach did not take into account the small fields generated by the various branch circuits that may reside in the area directly behind the magnetic sensors. Fourth, the previous approach was only able to infer apparent power and not true power since it does not take into account the phase information between the voltage and current waveforms. This is an important limitation as it is not able to accurately infer power use of highly inductive loads, which now tends to constitute much of the power consumption in a modern home (CFS, LEDs, HVAC, Computers, TVs, etc). In addition, researchers in the energy disaggregation community have limited utility with just the apparent power data.

In this work, we have significantly improved over previous work by introducing a self-calibrating technique that dynamically generates a multi-order transfer function between the magnetic sensors and the actual current across the entire range of power use in the home. Instead of mathematically modeling the transfer function *a priori*, we use a learning approach to generate this transfer function for each home, which is less susceptible to differences in breaker panel design and construction. In addition, it removes the need for precise placement of the sensor because it takes into account “interference” from any branch circuits. Prior work has also assumed that a plug-in calibrator would draw known power loads to fit a transfer function. However, the drawback of this approach is that it assumes the calibrator is able to draw a large range of loads (~0-20 kW) depending on the size of the home and types of appliances present. This is impractical because of safe heat dissipation limitations in addition to being difficult to build it in a small form factor. In this work, we introduce a technique that uses a calibrator with a much smaller range (0-300 W) by leveraging the insight that we can use a home’s natural electrical activity throughout the day as a part of the self-calibration sequence.

The main contributions of this work are as follows:

* This approach has the ability to predict the phase angle between the current and voltage to infer true power. This is equivalent to predicting the waveform itself and not just the magnitude.
* A self-calibrating approach that does not require precise placement of the sensor on the breaker panel and uses the actual power use throughout a day for calibration.
* A neural network-based learning approach that dynamically generates a multi order magnetic sensor transfer function.

Through deployments in six homes and one industrial building we show that this new approach can predict RMS current and phase angles with an accuracy of 96.0% and 94.3%, respectively. Overall it can predict real power consumption with an accuracy of 95.0% in real-world use. We also evaluated our technique by placing the sensors in different non-ideal positions on the panel and achieved an accuracy of 97.4% across all the placements.

# RELATED WORK

There are many commercially available sensors for measuring and showing appliance level energy use at each outlet, such as the Conserve Insight™, GreenSwitch, and Kill-A-Watt™. In case of whole house power consumption, some of the popular commercially available solutions are The Energy Detective and (TED®) and the PowerCost Monitor. Installing TED involves placing a CT around the main electrical feeds (mains) *inside* the breaker panel, which requires a professional installation due to high-voltage shock hazard. On the other hand, PowerCost can easily be installed by a homeowner without hiring an electrician, but requires either electromechanical meters or electronic meters with an exposed and compatible optical port. Hence it is constrained to specific type of meters with its update rate as well as performance dependent on the meter and exposed data ports of the same.

Because of such limitations, contactless solutions are emerging that try to infer power without having direct access to the mains. Cooley *et al*. [5]describes one such solution that measures the current at individual circuit breakers using a magnetic sensor placed on the face of the breaker switch itself. While this approach is promising, most electric codes do not allow anything to be placed on the circuit breakers for extended use because of the potential interference with its life-saving cutoff operation. In addition, a sensor would have to be placed on each circuit breaker to gather whole home power use or on the main circuit breaker, if present. Lorek *et al*. [10] also describes a similar magnetic field based approach where a magnetic sensor have to be placed on every breaker switch on the panel. In addition to requiring a number of sensors, this system also needs to be calibrated manually by the homeowner, which might be impractical and extremely difficult for a homeowner to perform.

Patel *et al.* proposed a solution that uses a pair of magnetic sensors placed on the face of the breaker panel (instead of the breakers) to sense the current flowing through the main bus bars [11]. A set of LEDs were used to help guide the user on placement. Similar to our approach, this system also used a load calibrator to create a transfer function. However, they assumed a linear transfer function and that the calibrator could emulate the entire power range of the house. Despite the use of LEDs to help with placement, other branch circuits and stray wires impact the magnetic field under the sensors. In our investigations, we found that the state of the magnetic flux changes throughout the day as various appliances are used. This means that the LEDs only help if the breaker panel state remains the same after the initial installation. Also, the previous approach only inferred apparent power and didn’t take into account the phase angle between current and reference voltage.

To overcome these limitations, we use a calibrator with smaller loads and leverage the natural household electrical activities throughout the day to generate a transfer function for the entire range of power use in the home. Because of the in situ dynamic model, our system is not limited to perfect placement of sensors. In addition, because of the capability of predicting absolute current waveform, we can also calculate phase angle in real time. To the best of our knowledge, this is the first attempt to solve the problem of calculating phase angle using a single set of magnetic sensors.

This work would allow researchers in the energy disaggregation community easy access to power data in a home without the need for professional installation. Many approaches have been developed that use power usage analysis to infer appliances use [1,6,7,13]. Approaches that use alternative ways to infer appliance could use our approach to associate the actual power use to each inferred appliance event [2,4,8,12].

# system descripton and algorithmic details

Breaker panels in the U.S. comply with the General Electric “style” based on the guidelines from National Electrical Manufacturers Association (NEMA). Briefly, there is a front surface with an access door that covers the interior where main electrical feeds or lines are connected to the bus bar. In this work, we have focused on typical U.S. breaker panels such as the shown in Figure 2, however the approach presented in this paper can scale to varying designs of breaker panels and to those in other countries as our learning approach is dynamic and calibrates in-situ.

## Theory of Operation

Our sensing approach involves computing the current consumption in the home by inferring the current being drawn through the main feeds/legs coming in the home at the breaker panel. In general, most homes in the U.S. have split single-phase electrical service where each leg is 180 degrees apart from each other. Industrial buildings usually have three-phase service where three phases are 120 degrees offset from each other. In either case, we need to predict the current flowing through all the legs. The field generated from the main legs allows us to estimate the current flow through each leg separately, which radiates a few centimeters from the wire and even through the layer of sheet metal. In the ideal situation, magnetic field scales linearly with the current. However this relationship is not as simple in practice because of fields from all neighboring wires, reflected magnetic fields, and magnetic nonlinearities of the sheet metal.




Figure 2: Interior of a typical U.S. three-phase breaker panel. Three main feeds are connected to the bas bar. Split-phase systems have two electrical feeds instead of three.


To sense the radiated magnetic field, we use a set of magnetic pickup sensors placed on the outside of a breaker panel. To convert this sensed magnetic field to current, we need to determine a transfer function, *i.e*., given the sensed magnetic flux, determine what the underlying current flow in the main leg is that induces the flux. We infer this function using a calibrator plugged in an electrical outlet that draws a known amount of current (by powering a resistive load) at a given time while the sensor senses the change occurring in the magnetic field due to that current draw. In practice, we imagine the calibrator embedded in an in-home energy display.

At first we create an initial transfer function using this collected calibration data which only works for a small range (limited to the range of loads the calibrator can provide) of magnetic field values. We store this range as calibrated region while keeping track of the present magnetic sensor values. These values change over time as appliances are used in a home. Every time these values reach an un-calibrated region, the calibrator is commanded to pull a small load. The difference in the observed magnetic field signal at that level is used to update the transfer function.

In the rest of this section, we describe the hardware and software of our prototype implementation. We primarily focus on the intuition behind using a machine-learning model and describe its use in creating a dynamic transfer function. It should be noted that during the rest of the description, we assume a home environment having two-phase power supply, however our system scales to a three-phase industrial setting as well.

## Hardware

Our prototype system consists of two components: a *Sensor unit* and a *Calibration unit*. Figure 1 shows a sample placement of the sensor unit on a breaker panel. The data from this unit is collected using a DAQ (National Instruments USB-6259) connected to a laptop. Figure 4 (a) shows a calibration unit installed in an electrical outlet. The calibration unit is also connected to the same laptop. The laptop sends the control logic to the calibration unit based on the captured data from DAQ.



**Figure 3: The sensor unit consists of four magnetic pickup sensors surrounded by some permanent magnet.**

### Sensor Unit


The sensor unit (see Figure 3) consists of four magnetic pickup sensors (we use RadioShack removable telephone pickups. Model no: 07C12) surrounded by permanent magnets. The sensors detect magnetic field generated from the 60 Hz current flow from the legs behind the panel (as well as some of the branch circuits). The surrounding magnets are placed to reduce the effect of magnetic nonlinearity of the sheet metal located in between the main lines and magnetic sensors. Briefly, the time difference between the actual current waveform and sensed magnetic waveform is depended upon the magnetic saturation and permeability of the material. Saturating the magnetic field reduces the nonlinearity induced by the sheet metal. In other words, the nonlinearity of the phase difference between the actual and sensed waveform reduces, which plays a key role during the phase angle calculation. We discuss the effect of this phenomenon later in the deployment and results section.

### Calibration Unit

Our system consists of two calibration units installed in two different outlets, each on a different leg. Each unit briefly draws a series of known loads (0-300 W) for automatic calibration described before. It also senses the line voltage for calculating true power.

The calibration unit consists of four high wattage resistors (we use Ohmite chassis mount resistors. Part no. TGHLVR100JE) connected in several series and/or parallel combinations through a set of relays. A microcontroller drives the relays to provide 25 W, 100 W, 200 W, and 300 W loads.

Figure 4(b) shows a zoomed in view at the calibration unit. It should be noted that in previous work, Patel *et al.* [11] also used a calibrator to model step power changes. However, they made an assumption of the calibrator pulling a load up to ~20 kW depending on the appliances present in a home, which is impractical to build in practice because of the large and unsafe heat dissipation requirements. In contrast, our calibrator only pulls up to 300W and leverages the actual electrical activities in the home to calibrate the entire range.

**Figure 4: *Left:* Calibrator unit installed in one of the outlets; *Right:* Closer look at the calibration unit**

## Software Implementation Details

The four magnetic sensors (S1, S2, S3, and S4) shown in Figure 3 sense the magnetic field generated from each leg of the breaker panel. Our goal is to generate a transfer function that converts these magnetic fields into current waveforms flowing through only each of the main legs. Since we are interested in predicting real power, we need to predict both the RMS value of the current waveform and phase angle between the current and voltage waveform. Therefore we decided to predict the current waveform instead of just the RMS value.

Creating a transfer function to compute the current waveform given the magnetic flux is non-trivial because of challenges posed by fundamental characteristics of breaker panel and the sensed magnetic field:

* *Stray Magnetic Flux*: In addition to the main feeds, breaker panel also consists of other electrical wires going through all the breaker switches. There are also wires passing around the main lines and each of those radiates good amount of magnetic field depending on the current flowing through them. Figure 2 shows a sample illustration of this situation. The magnetic pickup sensors catch the magnetic field radiated from all them. However, we are only interested in the magnetic field radiated from the main lines. All the magnetic field radiated from the surrounding wires need to be eliminated during the prediction. In other words, the transfer function should be able to identify flux changes caused only by the two main legs.
* *Position of Sensor*: The amount of magnetic field sensors receive depends on the distance between the legs and sensors. Our goal is to create a placement invariant system that works on any position of the breaker panel. Hence the transfer function should accommodate any distance between the legs and sensors.
* *Isolating flux from each main leg*: Current flowing through each line contributes to the sensed magnetic field of all four sensors. However, we don’t know a priori how much each line contributes to each sensor. For example in Figure 3, the leftmost and rightmost magnetic sensors are probably influenced mostly by the leftmost leg and rightmost leg, respectively. But the ratio of influence is unknown. For the two middle sensors, the scenario is even more unpredictable. The transfer function should be able to figure out the ratio by which each leg influences each sensor.
* *Breaker panel wiring uncertainty*: Finally, despite having guidelines from NEMA and NEC, internal wiring of breaker panels varies a lot among each other depending on the skill of the electrician who installed it. The transfer function should be able to work with any breaker panel with any type of wiring.

Because of all these characteristics that vary across different breaker panels, same amount of electrical load induces different amounts of magnetic field in different panels. In fact even in the same panel with the same positioning of sensor unit, the relationship between load and magnetic field depends on the existing magnetic field inside the whole panel. For example, let us say that the baseline current through one leg is I1 and a positive change of Ich amount results in a positive change of Sch1 in S1. If the baseline current changes to I2, the same positive Ich change will cause a different amount of change Sch2. Depending on how the magnetic fields radiated from different wires and their constructive or destructive interference, the value of Sch2 could even be negative despite a positive Ich value.

In summary, the relationship between the electrical current and sensed magnetic field is nonlinear and depends on the existing baseline magnetic field and presence of other magnetic fields. To accommodate this variability and nonlinearity, we observed that we can create multiple polynomial equations for each “state” of the breaker panel. Thus, if we can define the state in terms of magnetic flux, we can build a function for each state. Such a problem is well suited for applying machine-learning techniques; when given a state as inputs, we need to learn a function. We use a neural network as it essentially learns a polynomial function to predict output (electrical current) from input (magnetic flux states).

### Constructing Neural Network Model Using the Calibrator

As we mentioned previously, the calibrator can cycle through a series of 25 W, 100 W, 200 W, and 300 W loads. Right before the calibrator turns on a load, the system starts tracking the sensor values. Once the load is on, it causes a change in the total current and in-effect the magnetic flux. This change in flux is recorded by the system. Therefore for each calibrator action, our system constructs a training instance for the neural network. Structure of such an instance is shown in Figure 5. First 8 columns of every row are features to the learning algorithm. 9th column is the output value that the algorithm will try to learn. The neural network consists of one input layer, one output layer, and two hidden layers having five neurons in each of the layers.

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ***S1p*** | ***S1c*** | ***S2p*** | ***S2c*** | ***S3p*** | ***S3c*** | ***S4p*** | ***S4c*** | ***Ich*** |

Figure 5: Structure of a training row. First 8 columns are inputs and 9th column is output.

Here *S1p, S2p, S3p, and S4p* are the RMS values of four sensors before the calibrator turns on the load. *S1c, S2c, S3c, and S4c* are RMS values after the calibrator turns on the load. *Ich* is the amount of current the calibrator added to the leg where it is plugged-in. Note that as the relationship between magnetic flux change and electrical current change depends on the existing magnetic flux present in the panel; we take both previous and current magnetic flux as our features instead of just taking the change of flux.

In our implementation, the calibrator turns on each load for five seconds. Therefore after five seconds when the calibrator turns off the load, the system captures a similar event and calculates a similar training instance for the turn-off event. It must be noted that we never have access to the absolute value of current going through each leg. The only a priori information is the amount of current change the calibrator is intended to cause to the leg. Consequently, our neural network will only be trained to predict the change in current value, not the absolute current value.

However, our goal is to predict absolute current waveform going through each leg. To achieve this, we use a geometric translation technique that leverages the prediction model and natural electrical activities in a home to create a transfer function that converts sensor values to current waveform. Below is the description of our technique. For the sake of simplicity, we assume one magnetic sensor instead of four and one leg instead of two.

### Creating the transfer function

Once the system starts, the only information it knows is the current RMS magnetic field of the sensor (*Sk*). Initially the calibrator pulls a series of 100 W, 200 W, and 300 W loads (3 times each) on top of this field. Hence the field value changes and the system keeps track of the maximum value of the sensor (*Sk+1*). Now from *Sk* to *Sk+1*, it has 9 calibration events. For each event, there are 2 training instances (one for on event and one for off event) as mentioned before. Therefore it gathers 18 training instances from sensor value of *Sk* to *Sk+1* and uses these instances to train the neural network model described earlier.

This results in a function (*Fk*) that can convert magnetic field change value from *Sk* to S*k+1* to current change value *Ich­* (see Figure 6(a)). The goal is to find a function *F* that can convert any magnetic field value *S* to absolute current value *I.* Therefore the function *Fk* is placed into appropriate position of *F*. As already mentioned, the system never knows the absolute value of *I*, thus, a random y-axis value *R* is assumed and the function is placed on (*Sk, R*) position. Figure 6(b) shows an illustration of this approach.




Figure 6: (a) Predicted function from a small range of sensor values (Sk – Sk+1). (b) Placing the function in appropriate position.


Now the system does not know how the function looks like from *0* to *Sk* position. Therefore the function is extrapolated from (*Sk, R)* to (*0,0)* asshown in Figure 6(b). Obviously this region does a poor job in translating *S* to *I.* Therefore the system waits until the value of *S* falls below *Sk*, following which the calibration process is reinitiated. Just as before, it results in a new function (*Fj*) that can converts magnetic field value from *Sj* to S*j+1* where *Sj*< *Sk*. Now if *Sk < Sj+1*, the system combines *Fj* with *Fk* and creates a new function that covers from *Sj* to *Sk+1* (Figure 7(a)). Otherwise it keeps two separate functions *Fj* and *Fk* that covers ranges from *Sj* to *Sj+1* and *Sk* to *Sk+1*, respectively (Figure 7(b)).

As evident in Figure 7(a), the new extrapolated region is from *0* to *Sj*. If the sensor value ever falls below *Sj* (*e.g.* during night when most of the appliances are off), the system will initiate a new calibration cycle for the new region. Consequently, the system will recreate the whole function from the new position to Sk+1.

On the other hand in Figure 7(b), the new extrapolated regions are from *0* to *Sj andSj+1* to *Sk.* In case the value of sensor is *Sm* where *Sj+1* < *Sm <Sk*, the calibrator will trigger again and the system will create a new function from *Sm* to *Sk+1*. Note that this time the calibrator will only extrapolate from *Sm* to *Sj+1* as the system already has a function from *Sj* to *Sj+1*.

Similarly, if more appliances are turned on and the sensor value (*Sn*) exceeds *Sk+1*, the calibrator will trigger and the system will create a new function from *Sn* to *Sn+1* (Figure 7(c)). Again the system will only extrapolate from *Sn* to *Sk+1* as it already has a prediction function from *Sj to Sk+1*. In other words, as time goes by, the extrapolated regions will shrink more and more and the system will have a better translation function from *S* to *I.*

In summary, the key idea is that as the system runs in a house, it captures the usual electrical activities that increasingly provide it with a wide range of sensor values to learn from. As more appliances are turned on and off, the system gets a chance to calibrate for more and more ranges and the prediction function gets increasingly accurate. We will discuss the calibration requirement more in the results section.




**Figure 7: (a) Combined function: *Sj* - *Sk+1*. Extrapolated region: *0 - Sj* (b) Two separate functions: *Sj* – *Sj+1 & Sk* – *Sk+1*. Extrapolated regions: *0 - Sj* & *Sj+1 – Sk* (c) New function: *Sn-Sn+1*. Extrapolated regions: *0 - Sj* & *Sk+1 – Sn*.**

# Analyzing transfer function

### **Prediction using the transfer function**

Once the system starts, it creates a function *F* that takes four magnetic field values from four sensors (*S1, S2, S3, S4*) and translates them into current waveform *I*. Figure 8 shows a sample output of the prediction function *F.*


****Figure 8: (Top) Four waveforms from four sensors *S1 (blue), S2 (green), S3 (yellow), S4 (red)*; (Bottom) Predicted current waveform *I.***

As shown in the Figure, the system is able to predict raw current waveform flowing through each leg. In other words, it can predict both the RMS current (*I*) and phase angle (*θ*) between the line voltage and current waveform. Predicting this *θ* is very important from an energy monitoring perspective as it can tell us the real power consumed by the household as oppose to apparent power.

### **Phase Angle (θ) Prediction Analysis**


To predict phase angle *θ,* we rely on the following hypothesis:

*“Any change into the phase of the current waveform will also be reflected into the sensor waveform.”*



**Figure 9: (Top) Current and voltage waveform are almost in phase. (Bottom) Two waveforms (*blue* and *red*) are following the current waveform*.***

Figure 9 shows an example of the validity of the hypothesis. From the top graph, we see that voltage and current waveform are closely in phase with each other (*θ* is small). If we carefully inspect the bottom graph, we can see that two of the magnetic waveforms (*blue* and *red*) have the same phase characteristics (zero crossing rise and fall in almost same timestamps) as the current waveform. In other words, our prediction function will have more influence from these two sensors while predicting current waveform.




**Figure 10: (Top) Current waveform is lagging the voltage waveform. (Bottom) Two waveforms (*blue* and *red*) are still following the current waveform*.***

Figure 10 (top) shows us a different scenario where the current waveform is lagging the voltage waveform by an angle *θ.*  From the bottom graph, we can see that blue and red waveforms are also following the current waveform. In other words, when current waveform is phased shifted by angle *θ,* four sensor waveforms will also get phase shifted by some angles *θ1, θ2, θ3, and θ4.* Obviously these angles will be different from the original phase shift *θ.* But the sensors that are mostly influenced by the current waveform will have a closer shift to the angle *θ.* Thereforethe difference (*θdiff*) between real shift and sensed shift will be small.

However due to the presence of the sheet metal between the main lines and magnetic sensors, the phase difference (*θdiff*) between the actual current waveform going through the lines and magnetic waveform sensed by the sensor becomes a nonlinear function of magnetic saturation and permeability of the material. The surrounding magnets built into our prototype sensor unit are intended to saturate the magnetic field and reduce the nonlinearity effect. As a result, *θdiff* becomes near constant and the transfer function predicts the phase angle with good accuracy. We discuss the accuracy of this phase prediction approach more in the next section.

### **Visualizing the transfer function**

Mathematically, the transfer function can be expressed as follows: . As the function is 5 dimensional (4 inputs and one output), it’s hard to visualize the effect of each sensor on the prediction output. Therefore we decided to decompose the visualization using results from each sensor. Figure 11 shows the result. For each of the first four plots, we change one sensor (*S1/S2/S3/S4*) value from 0 µT to 100 µT linearly keeping all the other sensor values to 0 µT. The bottom plot assumes all the four sensors increasing from 0 µT to 0.05 µT.

**Figure 11: Decomposed transfer function. Top four plots show predicted current (*I*) based on just one sensor value (S1, S2, S3, and S4). Bottom one shows the plotting of *I* based on all four sensors.**

Though the plotting is not ideal (in actual case, the current is predicted based on different combinations of all sensor values), it gives us certain interesting insight. As an example, after a certain field value, the predicted current values go down for all the sensors except S1. This phenomenon is observed because of the presence of multiple magnetic waveforms inside the panel. As the phases of these waveforms are different and they are always changing based on load condition, there are constructive and destructive interferences in different locations inside the panel. Hence depending on the location of the sensor placement on the breaker panel, some sensor senses destructive interferences when there is a positive change in the current waveform and exhibits an inverse relationship between current and magnetic field.

If we inspect the bottom plot where all the sensor values are increasing, we find an interesting similarity between this plot and the topmost plot where only *S1* is increasing. Although for all the other three sensors, the current (*I)* is decreasing after a while; it is always increasing in case of the bottommost graph. Essentially, this behavior means that the transfer function is mostly influenced by S1. In other words, this sensor reflects the current waveform more precisely than other sensors. The neural network learns that and increases the coefficient of this sensor more than other sensors. Therefore the amplitude and phase of the predicted current is mostly determined by S1. This is one reason why a machine learning based approach is more appropriate for this kind of problem, since it would be nearly impossible to fit a single polynomial for these observations.

# In-home deployment and evaluation

To validate our technique, we conducted experiments in six different homes and one industrial building. Homes had two-phase wiring system and industrial building had three-phase system. We collected data from one house for a longer period, spanning seven days and from other places for a shorter period (spanning two days). This allowed us to show the general applicability of our system to a diverse set of breaker panels as well as the longer-term temporal stability of our solution. Table 1 shows the summary of the homes used in our evaluation.

|  |  |  |  |
| --- | --- | --- | --- |
| **ID** | **Panel type** | **Style/Built/Remodeled** | **Size/Floors** |
| H1 (\*) | Two-phase | Apartment/ 1993/NA | 550 sq. ft./ 1 flr. |
| H2 | Two-phase | House/1972/2002 | 1250 sq. ft./ 1 flr. |
| H3 | Two-phase | Apartment/ 1931/1994 | 800 sq. ft./ 1 flr. |
| H4 | Two-phase | House/1960/NA | 2220 sq.ft./ 1 flr. |
| H5 | Two-phase | House/1987/NA | 1340 sq. ft./1 flr. |
| H6 | Two-phase | House/NA/NA | 1452 sq. ft./1 flr. |
| I1 | Three-phase | Industrial Building/2003/NA | NA |

## It should be noted that all of our data collection sessions were performed under a naturalistic setting. That is, we did not give the homeowners any instructions on the use of their electrical appliances or requested any changes in their daily routines and household tasks. Once installed, our system ran in background for the entire data collection session with no participant interaction at all.



Data Collection Procedure

Our system was packaged such that it could be rapidly setup in a home. The sensor unit was placed on a breaker panel using double-sided tape. To collect the ground truth, we installed a commercially available transformer-based split-core current transformer (CT) inside the breaker panel prior to installing our sensor unit on the outside of the breaker panel. Both the sensor unit output and CT output were collected using the same DAQ device.

We used long extension cables to bring the two different outlets of different phases closer to the laptop. We then plugged in the two calibrators in the outlets. The calibrators and the data acquisition device were connected to a laptop. The laptop controlled the calibration unit, recorded all the data from the data acquisition device, and performed all the algorithmic processing in real-time. We just recorded the original and predicted waveforms for post-experiment analysis. The whole software portion was written in Matlab and Python.

## Deployment Results

### Accuracy Measurements

For each of the deployments, we calculated the RMS current value in ampere, RMS line voltage in volts, and phase angle of the current waveform with respect to voltage in degree every second. These quantities are recorded both for ground truth current waveform (measured from the CTs) and predicted current waveform (output from the algorithm). Finally we calculate the real power consumption for both of them in every second as follows: . It should be noted that during accuracy calculation, we only considered the accuracy of calibrated regions. However after a certain time, most regions became calibrated and all of the data were taken into consideration.

### Results

Our system requires installing two calibrators in two different phases of a house. Then, based on the calibrator data, it creates two different functions *F1* and *F2* for two phases *P1* and *P2*. During the evaluation, we also considered the case of using just one calibrator in one of the phases. Therefore for each home, we calculated the accuracy for all three possible cases: using just one calibrator in *P1*, using just one calibrator in *P2*, and using both calibrators in both phases. It should be noted that during all of our deployments, both calibrators were installed in both of the phases all the time. But as we recorded both of the functions *F1* and *F2* for *P1* and *P2*, respectively; we just used *F1* to predict current in both *P1* and *P2* and *F2* to predict current in both *P1* and *P2*. Table 2 shows the summary of all the deployment results.

From Table 2, we see that the average accuracy across all the deployments while using two calibrators is 95.0%. This shows the robustness of our system in predicting real power across different breaker panels and placement. It should be noted that [11] achieved an accuracy of 97.36%, however Patel *et al.* only calculated apparent power step changes in a controlled environment with a few fixed appliances while our experiments calculated accuracy with real power obtained in real environment with natural electrical activities for longer durations.

|  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **ID** | **Deployment time (Hour)** | **Power Range (Watt - Watt)** | **Using both phase calibration (%)** | | | **Using Phase 1 Calibration (%)** | | | **Using Phase 2 Calibration (%)** | | |
| **IRMS (Amp)** | ***cosθ*** | **Power (Watt)** | **IRMS (Amp)** | ***cosθ*** | **Power (Watt)** | **IRMS (Amp)** | ***cosθ*** | **Power (Watt)** |
| **H1 (\*)** | 168 | 252 - 4952 | 98.1 | 96.8 | 96.2 | 90.3 | 88.4 | 89.1 | 86.7 | 86.4 | 86.1 |
| **H2** | 48 | 396 - 6840 | 95.6 | 97.7 | 96.7 | 89.2 | 84.7 | 86.6 | 91.3 | 85.9 | 87.7 |
| **H3** | 48 | 598 - 6673 | 96.9 | 94.3 | 95.8 | 92.9 | 89.3 | 90.3 | 91.7 | 88.8 | 89.3 |
| **H4** | 48 | 707 - 12373 | 97.2 | 95.3 | 96.0 | 90.4 | 85.5 | 87.4 | 85.3 | 81.0 | 84.9 |
| **H5** | 48 | 441 - 5567 | 94.2 | 93.9 | 94.0 | 86.6 | 84.0 | 85.7 | 87.2 | 82.5 | 84.7 |
| **H6** | 48 | 311 - 4110 | 93.3 | 90.8 | 91.2 | 87.4 | 82.1 | 83.1 | 88.1 | 86.4 | 86.7 |
| **I1** | 48 | 1920 - 5982 | 96.8 | 91.6 | 95.2 | 83.1 | 78.3 | 80.1 | 84.3 | 81.1 | 82.9 |
| **Aggregate** | 456 | 252 – 12373 | 96.0 | 94.3 | 95.0 | 88.5 | 84.6 | 86.0 | 87.8 | 84.5 | 86.0 |

Table 2: In-home deployment results. The results are shown with two calibrators (one on each electrical phase) and a single calibrator (\* 7 days deployment).

# EVALUATION UNDER DIFFERENT CONDITIONS

## Effect of Placement on Accuracy

As we claimed earlier, our system does not rely on the precision of placement of sensors. In all of our deployments, depending on the structure of the breaker panel, we placed the sensor unit in different positions and the accuracy remained unaffected. To further analyze the positioning effect on accuracy, we conducted an experiment in a controlled environment. Creating a controlled environment for this experiment was necessary, as we did not want the accuracy to get affected by different electrical conditions.

### Controlled Experiment Environment

At first we decided to put the sensor unit at 6 different locations on the breaker panel (See Figure 12). For each of the locations, we maintained a controlled environment as follows:

First we made sure that the environment is electrically quiet and no appliances are being turned on or off. Then, we measured the baseline power consumption (C) of the environment. We then turned on a 300 W load from the calibrator 3 times on top of the baseline and created a prediction function that works from C W to C+300 W. After that we turn on a 100 W fan, which brings the baseline to C+100 W. As we already have a function that works from C to C+300 W, the prediction function should perform well for the current load condition.

After 10 seconds we turned the load off. We then turned on a 1300 W heater and went through the same procedure as described in the previous paragraph, that is, we calibrated the system from C+1300 W to C+1600 W. Finally, keeping the 1300 W load on, we turned on a 500 W rice cooker and repeated the same procedure to calibrate from C+1800 W to C+2100 W.


### Accuracy Results

Figure 12 shows the accuracy in each of the 6 positions. We observed that for all positions on the breaker panel, the minimum accuracy was 96.3% with an average accuracy of 97.4%. This experiment confirmed that our approach works independent of sensor position on the breaker panel with high accuracy.

## Accuracy without calibrator

The longer our system runs in a house; the number of calibrated regions becomes wider and more accurate. At the same time, the number of calibration cycle also gets less frequent. Once it covers the entire range for a house, the calibration frequency further decreases. Thus, as long as the power consumption resides within calibrated region, the calibrator could be turned off with little effect on the overall accuracy. To test this hypothesis, we performed an additional experiment.

First, we ran our system for 24 hours in a home with all the existing appliances and system calibrated the region from 247 W – 5344 W, yielding an overall accuracy of 95.7%. Next, we turned the calibrator off and introduced four new appliances (two bulbs of 125 W and 250 W, one fan of 100 W, and a heater of 700 W). We turned each of the appliances on, both individually and in combination while keeping the total power consumption within the calibrated range. This resulted in a small drop in accuracy yielding 94.2%. This experiment confirmed that even with the calibrator turned off and new appliances being introduced, the overall accuracy does not deteriorate much as long as the consumption resides within the previously calibrated region. Moreover, this experiment also shows that the generated function does not overfit based on existing appliances. It is flexible enough to work with any new appliance as long as the total consumption does not exceed the calibrated region.



### **Figure 12: Accuracy on different positions. Min accuracy: 96.3%. Average accuracy: 97.4%.**

# discussion and Conclusion

We presented a practical approach to automatically calibrating a stick-on real power meter which can be installed by the homeowner without requiring manual calibration. This system does not require professional installation service of opening the breaker panel and installing CTs around the main electrical feeds. To the best of our knowledge, the approach presented here is the first non-contact one to calculate phase angle between current and voltage waveform. This allows calculating real power as opposed to apparent power. In addition, our technique is also independent of sensor placement, which greatly reduces the installation effort required from end users. Most importantly, unlike the previous approach [11], our system is capable of predicting real-time, absolute power consumption in a home.

The in-home deployments show an average accuracy of 95.0% across seven different environments. This result is encouraging and acceptable for power monitoring applications considering that the accuracy of consumer whole-house energy monitoring devices is around 96%. We also evaluated our system with sensor placed at different positions on the breaker panel and achieved an average accuracy of 97.4%. These results show the potential of the system in becoming a practical and easily deployable solution for whole house power consumption sensor.

To assess the energy viability of using the self-calibration approach, we also calculated the energy dissipated by the calibrator across all of our deployments. On average the energy use per home is just 0.181 kWh for it to converge on the full transfer function. In our current prototype, we calibrate the system each time the consumption falls into an un-calibrated region. In future, we can easily envision using a threshold and calibrate only when the consumption falls outside the threshold region. This will reduce the amount of calibration cycle as well as the energy dissipation. Furthermore, our calibrator was designed to pull up to a 300 W load. However we found through post processing that it may be possible only go up to 50 W thus reducing the power needs during calibration.

For this prototype, we used four off-the-shelf magnetic pickup sensors. In the future, one can easily imagine building custom-made sensor arrays with inductors. Moreover, these pickup sensors are essentially inductors for all practical purposes. Hence with the recent advent of ubiquitous circuit printing techniques [9], we envision printing an array of inductors on a flexible substrate as magnetic pickup sensors and sticking them on a breaker panel just like a sticker. Finally, to show the result of our technique to end-user, a display unit is needed to be install in some outlet of the home. We can foresee packaging the calibrator within this display unit and remove the need for an external calibrator unit.

# REFERENCES

1. Abbott, R.E. and Hadden, S.C. Product Specification for a Nonintrusive Appliance Load Monitoring System. *EPRI Report# NI-101*, 1990.

2. Gupta, S., Reynolds, M.S., Patel, S.N., ElectriSense : Single-Point Sensing Using EMI for Electrical Event Detection and Classification in the Home. In Ubicomp 2010.

3. Shui, B. and Dowlatabadi, H. Consumer lifestyle approach to US energy use and the related CO2 emissions. *Energy Policy 2005;33*:197–208.

4. Chen, J., Kam, A.H., Zhang, J., Liu, N., and Shue, L. Bathroom Activity Monitoring Based on Sound. In Pervasive 2005, 47–61.

5. Cooley, J.J., Member, S., Vickery, D., Member, A.A., Member, Z.C., and Fellow, S.B.L. A Retrofit 60 Hz Current Sensor for Power Monitoring at the Circuit Breaker Panel. In 25th annunal IEEE APEC 2010.

6. Hart, G. Advances in nonintrusive appliance load monitoring. In *Proceedings of EPRI Information and Automation Conference*, 1991.

7. Hart, G.W., Nonintrusive Appliance Load Monitoring. Proceedings of the IEEE, 1992. 80(12): p. 1870-1891.

8. Ho, B., Kao, H.C., Chen, N., et al. HeatProbe : A Thermal-based Power Meter for Accounting Disaggregated Electricity Usage. In ubicomp 2011.

9. Kawahara, Y., Hodges, S., Cook, B.S., and Abowd, G.D. Instant Inkjet Circuits : Lab-based Inkjet Printing to Support Rapid Prototyping of UbiComp Devices. In ubicomp 2013, 363–372.

10. Lorek, M.C., Chraim, F., Pister, K.S.J., and Lanzisera, S. COTS-based stick-on electricity meters for building submetering. In *2013 IEEE Sensors*, (2013), 1–4.

11. Patel, S.N., Gupta, S., and Reynolds, M.S. The design and evaluation of an end-user-deployable, whole house, contactless power consumption sensor. In CHI 2010, 2471-2480.

12. Patel, S.N., Robertson, T., Kientz, J.A., Reynolds, M.S., and Abowd, G.D. At the Flick of a Switch : Detecting and Classifying Unique Electrical Events on the Residential Power Line. In Ubicomp 2007, 271–288.

13. Zeifman, M., Member, S., and Roth, K. Nonintrusive Appliance Load Monitoring : Review and Outlook. In IEEE Transaction on Consumer Electronics; Vol: *57*, Issue: 1, 2011, 76–84.